MEMORANDUM

To: Infrastructure leadership; Legal, Finance and Engineering reviewers      Date: October 7, 2026

From: [Your name]      Re: Where to site a first-phase hyperscale deployment (illustrative 50-100 MW IT load, energized 2028-2029)

Basis: public data as of Oct 2026 (EIA, CBRE, JLL, utility and state filings, trade press). Portfolio analysis, not employer data. Companion workbook: DC_Site_Scoring_Model.xlsx.

1. Recommendation

Lead with Dallas-Fort Worth for the first phase, targeting powered sites with a bridging-power plan. Keep Seattle/Quincy as the second option, best suited to latency-tolerant AI training. Do not plan new large-load capacity in Hillsboro or Northern Virginia on a 2028-2029 timeline. DFW ranks first in all six weighting scenarios (power-first, latency-first, cost-first, risk-first, speed-to-market, base) and stays first when every judgment-based variable is removed (sourced-data-only score: DFW 87, Seattle/Quincy 75, next best 44).

2. Results (18 variables, 7 categories; 0-100, relative to these six markets)

| Market | Base score | Rank range* | What drives it |
| --- | --- | --- | --- |
| Dallas-Fort Worth | 72.5 | 1 to 1 | Shortest reported time to power (~36 mo), lowest state industrial power price (6.12 c/kWh), most workable bridging-power options, central latency (~25 ms est.). 1.8% vacancy, 39.6 MW available. |
| Seattle / Quincy | 61.8 | 2 to 3 | Cheap, clean hydro and best climate. Held back by Grant PUD queue (~900 MW requested vs ~350 MW uncommitted), Seattle pause on >20 MVA, and highest latency (~42 ms est.). |
| Columbus | 47.3 | 2 to 4 | Ample water, good latency. AEP Ohio 85% take-or-pay, reported ~84-month timelines, tax exemption paused. |
| Phoenix | 41.1 | 4 to 5 | Highest hazard and water-stress scores, 3-year tax-exemption pause, APS has made no new data-center commitments since January. |
| Northern Virginia | 40.6 | 3 to 6 | Best network ecosystem, but ~7-year wait for 100 MW and 0.24% vacancy. Strong only if latency/ecosystem dominate. |
| Hillsboro / Portland | 29.7 | 5 to 6 | 0.21% vacancy, no contiguous 5 MW, 120-day moratorium, Schedule 96 contract terms, tax-break limits. |

*Best to worst rank across the six named scenarios. Categories: power and grid, market and pricing, network and latency, risk and resilience, policy and incentives, build and operations, growth headroom.

3. How robust is it?

- Sweeping the Power & Grid weight from 10% to 60% never changes the leader (DFW). A power-weight by latency-weight grid (15-45% by 5-30%) also leaves DFW first in every cell.

- Seattle/Quincy is second in five of six scenarios and slips to third only when latency is weighted heavily (Columbus 54.0, Seattle 52.9, Northern Virginia 52.8).

- Northern Virginia moves most with the weights (3rd to 6th): it is a latency/ecosystem play, not a power play.

4. Assumptions and limits

- Illustrative requirement: 50-100 MW, hyperscale or AI workload, lease or build. Scores are relative to these six markets only.

- About 49% of the base weight rests on analyst scores or estimates (tariff burden, grid cleanliness, local-approval risk, headroom, labor, climate, plus estimated time to power for Seattle and Hillsboro and estimated Seattle rent). Each is labeled in the Data sheet.

- Power prices are 2024 state averages; real large-load tariffs differ. Rents and vacancy mix brokers, size tiers and dates; Phoenix vacancy is mid-2025. Latency is a physics estimate, not a measurement.

- Official FEMA NRI county scores could not be pulled automatically; hazard scores combine NRI-based reporting with analyst judgment.

5. Risks to the DFW recommendation

- Queue and timing. ERCOT reports roughly 427-474 GW of large-load requests; its batch study began September 2026. Plan for slippage past 2028; one source says 24-36+ months from site acquisition to power.

- SB6 terms. Reported $50M of financial security per GW, study fees from $100,000, and curtailment rights during load shed for loads connecting after 2025.

- Little to lease. About 765 MW is under construction and roughly 95% preleased, and powered-land prices are rising; entitlement and rezoning timelines are long.

- Policy and hazard. Texas's sales-tax exemption is intact but reported as a possible 2027 repeal target; hail and flood exposure is high (2025 flooding affected substations in a major Texas market).

6. Open questions

- Legal: SB6 curtailment, disclosure and collateral obligations; take-or-pay floors (CBRE reports 60-85%) and triple-net structures; zoning and entitlement path; one aggregator lists a Texas action on new grid connections (3 Aug 2026) that I could not verify and should be confirmed with the PUCT.

- Finance: all-in cost per kW including NNN charges and power floors; funding interconnection deposits; value of the Texas exemption versus repeal risk; price of delay (every quarter late) versus a premium for earlier power; lease versus build.

- Engineering: latency tolerance of the workload (changes the weights and could favor Seattle/Quincy or Columbus); rack density and liquid-cooling conversion (over six months for retrofits); feasibility of behind-the-meter or bridging power; design for hail, flood and water use.

- Next steps: replace estimates with primary broker reports and the FEMA NRI download, request utility load studies for 3-5 DFW sites, and compare West Texas as an alternative (CBRE expects it to become a top-five market by 2028).